## Data Points Descriptions
# | Data Point | Description | Example | Asset Types associated with each data point | Required Field
1 | Equipment Identification Number | This field is to identify the D-11 identification number of the asset. Example: Follow D-11 equipment identification standards |  | Agitator_Mixers, Batteries, Boilers, Breakers, Burners, Cable, Compressors, Dampers_Isolation Gates_Penstocks, Fans, Filters, Gearboxes, Generators, HRSG, Heat Exchangers_Vaporizers, Instruments, Motors, Piping, Pulverizors, Pumps, Raceway, Skids, Tanks_Vessels, Transformers, Turbines, Valves | Required
2 | Equipment Description | This field is to identify the D-11 equipment description of the asset. Example: Follow D-11 equipment identification standards | C CLOSED CYCLE COOLING WATER HEAT EXCHANGER PRESSURE DIFFERENTIAL GAUGE | Agitator_Mixers, Batteries, Boilers, Breakers, Burners, Cable, Compressors, Dampers_Isolation Gates_Penstocks, Fans, Filters, Gearboxes, Generators, HRSG, Heat Exchangers_Vaporizers, Instruments, Motors, Piping, Pulverizors, Pumps, Raceway, Skids, Tanks_Vessels, Transformers, Turbines, Valves | Required
3 | Alternate ID 1 | This field is to identify Supplier identification if needed. Example: VENDOR-TAG-4452, LEGACY-P-22 | Supplier tag | Agitator_Mixers, Batteries, Boilers, Breakers, Burners, Cable, Compressors, Dampers_Isolation Gates_Penstocks, Fans, Filters, Gearboxes, Generators, HRSG, Heat Exchangers_Vaporizers, Instruments, Motors, Piping, Pulverizors, Pumps, Raceway, Skids, Tanks_Vessels, Transformers, Turbines, Valves | Required
4 | Project ID | This field is to identify the Southern Company project identification code of the asset. Example: BWN-CC-008 |  | Agitator_Mixers, Batteries, Boilers, Breakers, Burners, Cable, Compressors, Dampers_Isolation Gates_Penstocks, Fans, Filters, Gearboxes, Generators, HRSG, Heat Exchangers_Vaporizers, Instruments, Motors, Piping, Pulverizors, Pumps, Raceway, Skids, Tanks_Vessels, Transformers, Turbines, Valves | Required
5 | PSM asset? | This field is the answer (Yes or No) to whether the specific asset is a Process Safety Management asset. Example: Yes/No | Y/N | Agitator_Mixers, Batteries, Boilers, Breakers, Burners, Cable, Compressors, Dampers_Isolation Gates_Penstocks, Fans, Filters, Gearboxes, Generators, HRSG, Heat Exchangers_Vaporizers, Instruments, Motors, Piping, Pulverizors, Pumps, Raceway, Skids, Tanks_Vessels, Transformers, Turbines, Valves | Required
6 | Drawing Numbers | This field is to list all appropriate Southern Company or vendor drawings associated with the identified asset. Example: |  | Agitator_Mixers, Batteries, Boilers, Breakers, Burners, Cable, Compressors, Dampers_Isolation Gates_Penstocks, Fans, Filters, Gearboxes, Generators, HRSG, Heat Exchangers_Vaporizers, Instruments, Motors, Piping, Pulverizors, Pumps, Raceway, Skids, Tanks_Vessels, Transformers, Turbines, Valves | Required
7 | Manufacturer | This field is to identify the Manufacturer name (if available) of the asset. Example: |  | Agitator_Mixers, Batteries, Boilers, Breakers, Burners, Cable, Compressors, Dampers_Isolation Gates_Penstocks, Fans, Filters, Gearboxes, Generators, HRSG, Heat Exchangers_Vaporizers, Instruments, Motors, Piping, Pulverizors, Pumps, Raceway, Skids, Tanks_Vessels, Transformers, Turbines, Valves | Required
8 | Model Number | This field is to identify the Manufacturer model number (if available) of the asset. Example: |  | Agitator_Mixers, Batteries, Boilers, Breakers, Burners, Cable, Compressors, Dampers_Isolation Gates_Penstocks, Fans, Filters, Gearboxes, Generators, HRSG, Heat Exchangers_Vaporizers, Instruments, Motors, Piping, Pulverizors, Pumps, Raceway, Skids, Tanks_Vessels, Transformers, Turbines, Valves | Required
9 | Serial Number | This field is to identify the Manufacturer serial number (if available) of the asset. Example: |  | Agitator_Mixers, Batteries, Boilers, Breakers, Burners, Cable, Compressors, Dampers_Isolation Gates_Penstocks, Fans, Filters, Gearboxes, Generators, HRSG, Heat Exchangers_Vaporizers, Instruments, Motors, Piping, Pulverizors, Pumps, Raceway, Skids, Tanks_Vessels, Transformers, Turbines, Valves | Required
10 | Physical Location | This field is to mark coordinates of identified assets within Supplier design environment (3d models, etc.). Example: | floor/elevation/direction or coordinates | Agitator_Mixers, Batteries, Boilers, Breakers, Burners, Cable, Compressors, Dampers_Isolation Gates_Penstocks, Fans, Filters, Gearboxes, Generators, HRSG, Heat Exchangers_Vaporizers, Instruments, Motors, Piping, Pulverizors, Pumps, Raceway, Skids, Tanks_Vessels, Transformers, Turbines, Valves | If Available
11 | Mounting Position | This field is to describe the installed orientation of the equipment. Example: Vertical, Horizontal | vertical, horizontal | Gearboxes, Motors, Pumps | Required
12 | Spare Parts List | This field is to identify any spare parts lists or data points associated with the asset. If yes, indicate where located Example: Yes- Drawing#___, O&M Manual page___ | Y/N | Agitator_Mixers, Batteries, Boilers, Breakers, Burners, Cable, Compressors, Dampers_Isolation Gates_Penstocks, Fans, Filters, Gearboxes, Generators, HRSG, Heat Exchangers_Vaporizers, Instruments, Motors, Piping, Pulverizors, Pumps, Raceway, Skids, Tanks_Vessels, Transformers, Turbines, Valves | Required
13 | Type | This field is the D-11 equipment subtype Examples: Fans: axial, centrifical, Compressors: screw, positive displacement, recipicating, rotary vane, centrifugal, axial, scroll, diaphram Turbines: tandem, double flow, etc. HRSG/Boiler: package, startup, auxiliary, primary Agitator/Mixers: paddle, anchor, ribbon, etc. Gearboxes: helical, coaxial, bevel, parrallel, planetary, worm, spur Heat Exchangers/Vaporizors: shell/tube, plate, double pipe, air cooled, etc. Tanks/Vessels: pressure, non-pressurized, undreground, etc. Dampers/isolation gates/penstocks: guillotine, louver, flap, diverter Filters: cartridge, box, pleated Burners: duct, corner, registered, direct fire, air staged Pulverizers: ball mill, bowl mill, roll mill Valves: globe, spring , check, gate, ball, butterfly, diaphram | Examples: Fans: axial, centrifical, Compressors: screw, positive displacement, recipicating, rotary vane, centrifugal, axial, scroll, diaphram Turbines: tandem, double flow, etc. HRSG/Boiler: package, startup, auxiliary, primary Agitator/Mixers: paddle, anchor, ribbon, etc. Gearboxes: helical, coaxial, bevel, parrallel, planetary, worm, spur Heat Exchangers/Vaporizors: shell/tube, plate, double pipe, air cooled, etc. Tanks/Vessels: pressure, non-pressurized, undreground, etc. Dampers/isolation gates/penstocks: guillotine, louver, flap, diverter Filters: cartridge, box, pleated Burners: duct, corner, registered, direct fire, air staged Pulverizers: ball mill, bowl mill, roll mill Valves: globe, spring , check, gate, ball, butterfly, diaphram | Agitator_Mixers, Boilers, Burners, Compressors, Dampers_Isolation Gates_Penstocks, Fans, Filters, Gearboxes, Generators, HRSG, Heat Exchangers_Vaporizers, Instruments, Pulverizors, Tanks_Vessels, Transformers, Turbines | Required
14 | Material of Construction | This field is the primary construction material per design or datasheet. Example: Carbon steel, Stainless steel, Fiberglass, Cast iron, aluminum, PVC, etc. | charcoal, fabric, cs, ss | Agitator_Mixers, Burners, Compressors, Dampers_Isolation Gates_Penstocks, Fans, Filters, Generators, Heat Exchangers_Vaporizers, Motors, Piping, Pulverizors, Pumps, Tanks_Vessels, Valves | Required / If Available (varies by asset)
15 | Size | This field is the nominal size or rating per industry standard Example: 12in, 300 HP, 500KW | small, medium, large, 6", 12", kw, nozzle size, impeller size, overall dimensions | Agitator_Mixers, Boilers, Burners, Dampers_Isolation Gates_Penstocks, Gearboxes, Generators, HRSG, Piping, Pumps, Valves | Required / If Available (varies by asset)
16 | Diameter | This field is a measure of nominal diameter of piping or rotating component. Example: Inches, Feet | gates | Agitator_Mixers, Dampers_Isolation Gates_Penstocks, Filters, Motors, Pumps, Tanks_Vessels | Required / If Available (varies by asset)
17 | Length | This field is the overall length or installed length (including cable slack if applicable). Electrical - “Slack” length (in feet) added to the cable’s length in order to provide adequate cable for making terminations. Only use if relying on PDMS to calculate total cable length (see Table 5.3 – RACEWAY IMPORT FIELDS, “length” section). Defaults to 25ft. Example: | dampers | Agitator_Mixers, Dampers_Isolation Gates_Penstocks, Filters, Motors, Pumps, Tanks_Vessels, Cable, Raceway | Required / If Available (varies by asset)
18 | Weight | This field is a measure of installed equipment weight for rigging and maintenance planning. Example: Lbs, Tons | lb | Agitator_Mixers, Burners, Dampers_Isolation Gates_Penstocks, Pulverizors, Tanks_Vessels | If Available
19 | Depth | Equipment depth dimension (front-to-back). Example: In, Ft |  | Dampers_Isolation Gates_Penstocks, Filters | Required
20 | Width | Equipment width dimension (side-to-side). Example: In, Ft |  | Filters | Required
21 | Flow Rate | Design or operating flow through the equipment. Example: GPM, KPPH |  | Compressors, Dampers_Isolation Gates_Penstocks, Fans, Heat Exchangers_Vaporizers, Pumps, Valves, Pulverizors | Required / If Available (varies by asset)
22 | Design Pressure [PSIG] | Maximum allowable working pressure (MAWP) per design. Example: 150 PSIG |  | Compressors, Dampers_Isolation Gates_Penstocks, Fans, Generators, Pumps, Tanks_Vessels, Valves | If Available
23 | Exhaust Pressure [PSIG] | Pressure at discharge or exhaust outlet. Example: 18 PSIG |  | Turbines | Required
24 | Inlet Pressure [PSIG] | Pressure at equipment inlet under operating conditions. Example: 5 PSIG |  | Compressors, Fans, Filters, Pumps, Valves | Required / If Available (varies by asset)
25 | Maximum Pressure [PSIG] | Maximum pressure rating per code or OEM. Example: 300 PSIG |  | Boilers, Compressors, Dampers_Isolation Gates_Penstocks, Fans, Generators, Pumps, Tanks_Vessels | Required / If Available (varies by asset)
26 | Medium 1 Input/Output Pressure [PSIG] | Pressure of primary process fluid entering and exiting equipment. Example: 120 PSIG |  | Heat Exchangers_Vaporizers | Required
27 | Medium 2 Input/Output Pressure [PSIG] | Pressure of secondary process fluid (if applicable). Example: 120 PSIG |  | Heat Exchangers_Vaporizers | If Available
28 | Minimum Pressure [PSIG] | Minimum allowable operating pressure. Example: 2 PSIG |  | Compressors, Fans, Generators, Pumps | If Available
29 | Operating Pressure [PSIG] | Normal steady-state operating pressure. Example: 95 PSIG |  | Pumps | If Available
30 | Outlet Pressure [PSIG] | Pressure at equipment discharge. Example: 100 PSIG |  | Compressors, Fans, Filters, Pumps, Valves | Required / If Available (varies by asset)
31 | Pressure Range [PSIG] | Measurement or instrument range for pressure. Example: 0-300 PSIG |  | Instruments | If Available
32 | Design Temperature [F] | Maximum design temperature per code or datasheet. Example: 750 F |  | Boilers, Compressors, Fans, Generators, HRSG, Motors, Pumps, Turbines, Valves | If Available
33 | Exhaust Temperature [F] | Temperature at exhaust/discharge outlet. Example: 900 F |  | Turbines | Required
34 | Liquid Temperature [F] range | Operating temperature range of contained liquid. Example: 60-180 F |  | Transformers | If Available
35 | Medium 1 Input/Output Temperature [F] | Temperature of primary process fluid. Example: 450 F |  | Heat Exchangers_Vaporizers, Pulverizors | Required
36 | Medium 2 Input/Output Temperature [F] | Temperature of secondary process fluid. Example: 450 F |  | Heat Exchangers_Vaporizers | Required
37 | Operating Temperature [F] | Normal operating temperature of equipment. Example: 450 F |  | Boilers, Compressors, Fans, Gearboxes, Generators, Motors, Pumps | Required / If Available (varies by asset)
38 | Temperature [F] Range | Measurement range for temperature instruments. Example: 50-160 F |  | Instruments | If Available
39 | Winding Temperature [F] range | Allowable temperature range for electrical windings. Example: 150-230 F |  | Transformers | If Available
40 | Control Range | Operating/control range for modulating devices. Example: 0-100% | non manual | Valves | Required
41 | Cooling Type | Equipment cooling method per design. Example: Air Cooled, Water Cooled, Hydrogen Cooled | HP - 1, IP- , LP | Boilers, Compressors, Gearboxes, Generators, HRSG, Turbines, Transformers | Required / If Available (varies by asset)
42 | Coupling Type | Mechanical connection between driver and driven equipment. Example: Direct, Flexible, Grid |  | Motors, Pumps | Required
43 | Drive Type | Prime mover type supplying power. Example: Electric Motor, Steam Turbine, Gas Turbine | steam, gas, hydro | Dampers_Isolation Gates_Penstocks, Fans, Generators, Turbines, Motors, Pumps | Required / If Available (varies by asset)
44 | Enclosure Type | Electrical enclosure classification. Example: TEFC, ODP, Explosion-Proof |  | Fans, Motors | If Available
45 | Fuel Type | Primary fuel used in combustion equipment. Example: Natural Gas, Diesel, Coal | supplemental heat source, duct burner | Boilers, Burners, HRSG | Required
46 | Ignitor Type | Ignition system type for burners. Example: electric spark rod | electric, spark rod | Burners | Required
47 | Insulation Type | Type of insulation used on equipment or windings. Example: Fiberglass, Mineral Wool |  | Generators, Motors, Piping | Required / If Available (varies by asset)
48 | IO Type | Input/output or actuation type per D‑11. Example: Discrete, Analog, Manual | non manual | Valves | Required
49 | Lube Oil Type | Lubrication oil specification per OEM. Example: ISO VG 32, Synthetic Turbine Oil |  | Compressors, Fans, Generators, Turbines | If Available
50 | Mounting Type | Equipment mounting configuration. Example: Skid Mounted, Baseplate Mounted | pad, etc | Transformers | Required
51 | Protective Relay Type | Type of protective relay associated with the equipment. Example: Overcurrent, Differential, Distance Relay |  | Batteries, Breakers, Transformers | Required
52 | Spring Type | Type of spring used (typically valves or relief devices). Example: Compression, Tension | relief valves | Valves | Required
53 | Commodity Type | Two-letter PDMS classification used for asset grouping (Equipment, Cable, Raceway). Example: EQ, CA, RW | CA | Batteries, Breakers, Cable, Raceway, Transformers | Required
54 | Bearing Type | Bearing design used in rotating equipment. Example: journal, roller, ball | journal, roller | Compressors, Fans, Gearboxes, Generators, Pulverizors, Turbines | Required / If Available (varies by asset)
55 | Bus Type | Electrical bus classification. Example: Switchgear, MCC | MCC or switchgear | Batteries, Breakers | Required
56 | Horsepower | Rated mechanical power output of equipment. Example: 250 HP |  | Agitator_Mixers, Gearboxes, Motors, Pulverizors | Required / If Available (varies by asset)
57 | RPM | Rated rotational speed of equipment. Example: 3,600 RPM |  | Agitator_Mixers, Compressors, Fans, Generators, Motors, Pulverizors, Pumps, Turbines | Required
58 | Input RPM | Rotational speed entering a gearbox. Example: 900 RPM |  | Gearboxes | Required
59 | Output RPM | Rotational speed exiting a gearbox. Example: 900 RPM |  | Gearboxes | Required
60 | Supply Power Req'd | Electrical power supply requirements. Example: 480V / 3PH | voltage | Agitator_Mixers, Compressors, Fans, Gearboxes, Generators, Turbines | Required / If Available (varies by asset)
61 | Excitation voltage | Voltage used for generator excitation system. Example: 125 VDC |  | Generators | Required
62 | Voltage | Equipment operating voltage. Example: 4,160 V | terminal | Generators, Instruments, Motors, Batteries, Breakers | Required / If Available (varies by asset)
63 | Voltage in | Incoming voltage to equipment (e.g., transformer primary). Example: 13.8 kV |  | Transformers | Required
64 | Voltage out | Outgoing voltage (e.g., transformer secondary). Example: 4.16 kV |  | Transformers | Required
65 | Heater Voltage | Voltage supplied to heater elements. Example: 120V |  | Motors | If Available
66 | Motor Controller Voltage | Control voltage for motor/valve control circuits. Example: 120VAC | non manual | Valves | Required
67 | Power | Electrical or mechanical power rating. Example: 500 kW | max power | Gearboxes, Heat Exchangers_Vaporizers, Motors | Required / If Available (varies by asset)
68 | Locked Rotor Amps | Maximum current drawn at motor startup. Example: 600A |  | Motors | If Available
69 | Rated Amps FLA | Full load amperage rating. Example: 85A |  | Generators, Motors | Required
70 | Phase | Electrical phase configuration. Example: 3 Phase |  | Generators, Motors, Transformers | Required
71 | Power Factor | Ratio of real power to apparent power. Example: 0.85 |  | Generators, Motors | Required
72 | Torque Power | Torque produced by equipment. Example: 2,500 in-lb |  | Compressors, Generators, Turbines | If Available
73 | Heater Power | Heater element power rating. Example: 5 kW |  | Motors | If Available
74 | Amp Rating | Maximum current capacity. Example: 800 A |  | Batteries, Breakers, Transformers | Required
75 | Arc Flash Rating | Incident energy level for electrical safety. Example: 8 cal/cm² |  | Batteries, Breakers | Required
76 | Dual Fed | Indicates if equipment has dual electrical feeds. Example: Yes/No | Y/N | Batteries, Breakers, Transformers | Required
77 | MCR (Maximum continuous rating) | Maximum continuous operating capacity. Example: 500,000 lb/hr |  | Boilers | Required
78 | Stored Medium | Material or fluid contained in the system. Example: Water, Steam, Natural Gas |  | Dampers_Isolation Gates_Penstocks, Tanks_Vessels, Piping | Required
79 | Medium State | Physical state of process fluid. Example: gas, liquid |  | Piping | Required
80 | Capacity | Maximum storage or throughput capacity. Example: 1,000 gallons, 200 GPM | lb/hr | Agitator_Mixers, Motors, Pulverizors, Pumps, Tanks_Vessels, Transformers | Required / If Available (varies by asset)
81 | Capacity Rating | Rated capacity per manufacturer or design. Example: 50 MVA |  | Transformers | Required
82 | From Asset | Upstream equipment connected to this asset. Example: D-11 Equipment Name |  | Piping, cable | If Available
83 | To Asset | Downstream equipment connected to this asset. Example: D-11 Equipment Name |  | Piping, cable | If Available
84 | From Terms | Electrical or signal termination points (source side). Example: L1, L2, L3, NEUT BUS, GND BUS |  | Batteries, Cable | Required
85 | To Terms | Termination points (destination side). Example: A, B, C, N, G |  | Batteries, Cable | Required
86 | Wires | Conductors included in cable or circuit. Example: L1, L2, L3, N, G | L1, L2, L3, N, G | Batteries, Breakers, Cable | If Available
87 | Fail Mode/position | Default position on loss of power or signal. Example: Fail Open, Fail Close, Fail in Place | non manual - open/close | Valves | Required
88 | Filter Class | Classification of filter by service type. Example: Air, Oil, Water | air, water, oil | Filters | Required
89 | Filtration Rating | Particle removal size rating. Example: 10 microns | micron, inch, etc. | Filters | Required
90 | Gear Ratio | Ratio of input to output speed. Example: 2:1 |  | Gearboxes | Required
91 | Heat Trace | Indicates presence of heat tracing system. Example: Yes/ No |  | Piping | Required
92 | Insulation Spec | Insulation specification reference. Example: Spec-INS-01 |  | Piping, Generators, Motors | Required / If Available (varies by asset)
93 | Insulation Thk | Thickness of applied insulation. Example: 2 inches |  | Piping | If Available
94 | Internal Coating | Internal lining or coating system. Example: Epoxy Coated |  | Tanks_Vessels | Required
95 | Coating System | External coating or paint system. Example: ANSI 61 Gray |  | Piping | If Available
96 | Item | This field is for the number of individual cables represented by the cable tag. This number is used by PDMS to calculate total cable footage and terminations. Example: circuit CWPU650101 may be designed to include four individual 4/0, single conductor cables (three phases of power plus ground). In this case, the item field = 4. |  | Cable | Required
97 | Level | Elevation level reading or instrument value. Example: 75% |  | Instruments | If Available
98 | Loop No | Instrument loop identification number. Example: LIC-1001 |  | Instruments | Required
99 | PCB Containing Oil | Indicates presence of PCB oil. Example: Yes/ No | Y/N | Transformers | Required
100 | Relays | Relay types installed on equipment. Example: SEL-351, GE Multilin |  | Transformers | Required
101 | Safety Factor | Design safety margin factor. Example: 1.25 |  | Motors, Pumps | Required
102 | Service Factor | Motor service factor rating. Example: 1.15 |  | Motors | If Available
103 | Sections | Number of sections in equipment assembly. Example: 3,4,5 |  | Boilers, HRSG, Turbines | If Available
104 | Set Point | Target operating or trip value. Example: 150 PSIG | relief valves | Valves | Required
105 | Speed control | Method of controlling speed. Example: VFD, Variable Pitch |  | Fans | Required
106 | Spring Rating | Rated force capacity of spring. Example: 500 lb | relief valves | Valves | Required
107 | Torque | Rotational force applied Example: 3,000 in-lb | in/lb | Agitator_Mixers | Required
108 | Valve operator | Method used to actuate the valve. Example: Electric, Pneumatic | air, electric, motor, manual, hydraulic | Valves | Required
109 | Vector group | Transformer winding configuration. Example: Dyn1 |  | Transformers | Required
110 | # Poles | Number of poles in generator or motor. Example: 4 |  | Generators | Required
111 | Actuator Manufacturer | Manufacturer of valve actuator. Example: Rotork, Limitorque | non manual | Valves | Required
112 | Actuator Model Number | Actuator model per OEM. Example: IQ3 Pro | non manual | Valves | Required
113 | Actuator Serial Number | Unique actuator serial number. Example: SN-998877 | non manual | Valves | Required
114 | Cathodic Protection Req'd? | Indicates if cathodic protection is installed. Example: Yes/ No |  | Tanks_Vessels | If Available
115 | Links | This field is a continuity relationship established between raceways and/or equipment in PDMS. Linking two or more components establishes a logical path between them in which cables can be routed. Example: SMI003/MCCTA006, SMI003/PB001 | SMI003/MCCTA006, SMI003/PB001 | Batteries, Breakers, Cable, Raceway, Transformers | Required / If Available (varies by asset)
116 | Skid Reference/ID | Identifier for associated skid or packaged system. Example: SK-2001, Drawing #____ |  | Compressors, Fans, Generators, Instruments, Motors, Pumps | If Available
Note on B15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Add valve data point for internal material.

## D11 Equip code to asset matrix
Equipment Code | Description | Responsibility | Asset type
c | Agitator | Mech | Agitator_Mixers
MX | Mixer | Mech | Agitator_Mixers
BCS | Battery Containment System (Battery Electrical Storage) | Elec | Batteries
EB | Battery | Elec | Batteries
EBV | Battery/(DC) Voltage Balancer | Elec | Batteries
EC* | Battery Charger (Replace * with charger letter or number) | Elec | Batteries
EI | Electrical Inverter | Elec | Batteries
EU | UPS | Elec | Batteries
RCT | Rectifier | Elec | Batteries
RE | Electrical Reactive Equipment | Elec | Batteries
REG | Voltage Regulator | Elec | Batteries
RS | Electrical Resistor Equipment | Elec | Batteries
AX | Auxiliary Boiler | Mech | Boilers
BO | Boiler | Mech | Boilers
DS | Desuperheater / Attemperator | Mech | Boilers
AN | Annunciator | Elec | Breakers
ATS | Automatic Transfer Switch | Elec | Breakers
BD#* | Bus Duct (Replace # with voltage letter) (Replace * with bus letter or number) | Elec | Breakers
BKR# | Breaker – Standalone Breakers Only (Replace # with voltage letter) | Elec | Breakers
CP | Control Panel | Elec | Breakers
DSC# | Disconnect – stand alone (Replace # with voltage letter) | Elec | Breakers
EE | Miscellaneous Electrical Equipment (power supply, stand-alone starter, lighting, etc.) | Elec | Breakers
EP | Electrical Protection Equipment (breaker, HRG, CTs, PTs, etc.) | Elec | Breakers
FB#* | Fuse Box/Panel (Replace # with voltage letter) (Replace * with bus letter or number) | Elec | Breakers
FU# | Fused Switch (Replace # with voltage letter) | Elec | Breakers
HS | Electrical Local Control Station (single equipment control) | Elec | Breakers
LK# | Removable Link (Replace # with voltage letter) | Elec | Breakers
PB#* | Panelboard (Replace # with voltage letter) (Replace * with bus letter or number) | Elec | Breakers
PEEC | Packaged Electrical Equipment Center | Elec | Breakers
RP | Electrical Relay Panel | Elec | Breakers
SM | Switch Mode Power Supply | Elec | Breakers
SW | Electrical Switch | Elec | Breakers
TB | Termination Box | Elec | Breakers
AIG | Ammonia Injection Grid | Mech | Burners
BE | Burner Element | Mech | Burners
BG | Burner Observation Port | Mech | Burners
BT | Burner Equipment - tilts | Mech | Burners
BU | Burner | Mech | Burners
BZ | Burner Position Drive | Mech | Burners
IG | Ignitor | Mech | Burners
GND | Ground | Elec | Cable
LGT | Lighting | Elec | Cable
PLGE | Electrical Plug (stand-alone) | Elec | Cable
RC | Electrical Receptacle | Elec | Cable
RM | Revenue Watt-hour Meter | Elec | Cable
WR | Welding Receptacle | Elec | Cable
CO | Compressor | Mech | Compressors
AK | Air Cannon | Mech | Dampers_Isolation Gates_Penstocks
AL* | Air Lock (Replace * with the following letter:) D - Drop Through M - Metering | Mech | Dampers_Isolation Gates_Penstocks
DB | Classifier Distributor | Mech | Dampers_Isolation Gates_Penstocks
DP | Damper | Mech | Dampers_Isolation Gates_Penstocks
DVR | Diverter | Mech | Dampers_Isolation Gates_Penstocks
GF | Gate – Flow (conveying or airflow) | Mech | Dampers_Isolation Gates_Penstocks
GI | Gate – Isolation (conveying or airflow) | Mech | Dampers_Isolation Gates_Penstocks
IL | Injector Lance | Mech | Dampers_Isolation Gates_Penstocks
LVR | Louver | Mech | Dampers_Isolation Gates_Penstocks
PD | Pulsating Damper, Snubber | Mech | Dampers_Isolation Gates_Penstocks
BW | Blower | Mech | Fans
FCU | Fan Coil Unit (HVAC) | Mech | Fans
FN | Fan | Mech | Fans
IB | Injector Blower Assembly | Mech | Fans
PZ | Fan Blade Positioner (typically used on booster fans and ID fans) | Mech | Fans
SB | Sootblower | Mech | Fans
VNR | Ventilator | Mech | Fans
DQ | Dust Suppression / Collection | Mech | Filters
ESP | Precipitator | Mech | Filters
FL | Filter | Mech | Filters
HF* | Harmonic Filter (* = Nominal Voltage Class Letter) | Elec | Filters
HY | Hydroclone | Mech | Filters
MM | Mist Eliminator | Mech | Filters
OC | Oil Conditioner | Mech | Filters
PF | Purifier | Mech | Filters
RA | Electrical Precipitator Rapper | Elec | Filters
SN | Strainer | Mech | Filters
SZ | Screen | Mech | Filters
CM* | Electrical Communication Patch Panel / Equipment (Replace * with the following letter:) D-DCS (fiber patch panel for cabling and communication; located inside a DCS cabinet, a standalone panel, switchgear cubicle, etc.) N- Network Switches P-Public Address R-Protective Relaying S-Security / Surveillance T-Telephone | Elec | Gearboxes
GB | Gear Box | Mech | Gearboxes
HC | Hydraulic Coupling | Mech | Gearboxes
SG#* | Electrical Switchgear (Replace # with voltage letter) (Replace * with bus letter or number) | Elec | Gearboxes
BR | Generator Brakes | Mech | Generators
DG | Emergency Generator | Elec | Generators
GEN | Generator | Elec | Generators
HR | Heat Recovery Steam Generator | Mech | Generators
AC | Air Conditioner | Mech | Heat Exchangers_Vaporizers
AW | Air Washer | Mech | Heat Exchangers_Vaporizers
CD | Condenser | Mech | Heat Exchangers_Vaporizers
CDC | Condenser Cleaning System | Mech | Heat Exchangers_Vaporizers
CL | Cooling Tower | Mech | Heat Exchangers_Vaporizers
CU | Condensing Unit | Mech | Heat Exchangers_Vaporizers
DA | Deaerator | Mech | Heat Exchangers_Vaporizers
DH | Duct Heater | Mech | Heat Exchangers_Vaporizers
DU | Dehumidifier | Mech | Heat Exchangers_Vaporizers
DY | Dryer | Mech | Heat Exchangers_Vaporizers
HA | Air Heater | Mech | Heat Exchangers_Vaporizers
HM | Humidifier | Mech | Heat Exchangers_Vaporizers
HT | Electrical Heater / Heat Trace / Freeze Protection | Elec | Heat Exchangers_Vaporizers
HX | Heat Exchanger | Mech | Heat Exchangers_Vaporizers
UC | Unit Chiller | Mech | Heat Exchangers_Vaporizers
UH | Unit Heater | Mech | Heat Exchangers_Vaporizers
VPR | Vaporizer (Example: ammonia) | Mech | Heat Exchangers_Vaporizers
WH | Water Heater | Mech | Heat Exchangers_Vaporizers
AE | Analyzer Element / Probe | I&C | Instruments
AI | Analyzer Indicator (electronic) | I&C | Instruments
AR | Analyzer Recorder | I&C | Instruments
AIT | Analyzer Transmitter (Delete “I” if not indicating) | I&C | Instruments
BSS | Burner Switch (Scanner) | I&C | Instruments
BSIT | Burner Scanner Transmitter (Delete “I” if not indicating) | I&C | Instruments
CA | Console Bench Board | I&C | Instruments
CAL | Calibration Cylinder | Mech | Instruments
CB | Console Vertical Panelboard | I&C | Instruments
CC | Computer Cabinet (DCS/PLC – cabinet only) | I&C | Instruments
CE | Conductivity Element | I&C | Instruments
CI | Conductivity Indicator (Electronic) | I&C | Instruments
CON | Control System | I&C | Instruments
CR | Conductivity Recorder | I&C | Instruments
CIT | Conductivity Transmitter (Delete “I” if not indicating) | I&C | Instruments
DE | Density Element | I&C | Instruments
DI | Density Indicator (electronic) | I&C | Instruments
DR | Density Recorder | I&C | Instruments
DRV | Drive | I&C | Instruments
DIT | Density Transmitter (Delete “I” if not indicating) | I&C | Instruments
DX | Density Source (nuclear) | I&C | Instruments
EA | Electronic Alarm (horns and beacons) | I&C | Instruments
EM | Emission Monitoring (CEMS) | I&C | Instruments
ER | Voltage Recorder | I&C | Instruments
EIT | Voltage Transmitter (Delete “I” if not indicating) | I&C | Instruments
EY | Signal Isolator | I&C | Instruments
FE | Flow Element | I&C | Instruments
FG | Flow Gauge (mechanical, rotameter) | I&C | Instruments
FI | Flow Indicator (electronic) | I&C | Instruments
FM | Fiber Optic Modem | I&C | Instruments
FR | Flow Recorder | I&C | Instruments
FS | Flow Switch / High, Low (Append LL, L, H, or HH when needed) | I&C | Instruments
FIT | Flow Transmitter (Delete “I” if not indicating) | I&C | Instruments
GS | Sight Glass | Mech | Instruments
GT | Gas Detector | I&C | Instruments
IC | Instrument Cabinet | I&C | Instruments
IE | Instrument Enclosure (freeze protection) | I&C | Instruments
II | Current Indicator (electronic) | I&C | Instruments
IP | Instrument Panel | I&C | Instruments
IR | Current Recorder | I&C | Instruments
IS | Instrument Stand | I&C | Instruments
IIT | Current Transmitter (Delete “I” if not indicating) | I&C | Instruments
IT* | Current (Wireless Signal Converter) Transmitter (* = T for transmit signal to wi-fi) (* = R for receive wi-fi to signal) | I&C | Instruments
JI | Power Indicator | I&C | Instruments
JR | Power Recorder | I&C | Instruments
JIT | Power Transmitter (Delete “I” if not indicating) | I&C | Instruments
KC | Time Controller | I&C | Instruments
KI | Time Indicator | I&C | Instruments
KY | Event Sequencer | I&C | Instruments
LC | Level Controller | I&C | Instruments
LE | Level Element | I&C | Instruments
LG | Level Gauge | I&C | Instruments
LI | Level Indicator (electronic) (Append with U if programmable) | I&C | Instruments
LR | Level Recorder | I&C | Instruments
LS | Level Switch / High, Low (Append with LL, L, H, or HH when needed) | I&C | Instruments
LIT | Level Transmitter (Delete “I” if not indicating) | I&C | Instruments
ME | Moisture Element | I&C | Instruments
MI | Moisture Indicator (Electronic) | I&C | Instruments
MR | Moisture Recorder | I&C | Instruments
MIT | Moisture Transmitter (Delete “I” if not indicating) | I&C | Instruments
MTR | Meter, Density, Watt-hour | I&C | Instruments
OP | Operator/Engineer Station, Monitor, Video Display Unit, etc. | I&C | Instruments
PDS | Differential Pressure Switch / High, Low (Append with LL, L, H, or HH) | I&C | Instruments
PE | Pressure Element | I&C | Instruments
PD*T | Pressure (or Vacuum) Differential Transmitter (Replace * with I if indicating) | I&C | Instruments
P*G | Pressure (or Vacuum) Gauge (Mechanical) (Replace * with D if differential) | I&C | Instruments
P*I | Pressure (or Vacuum) Indicator (Electronic) (Replace * with D if differential) | I&C | Instruments
PO | Port (Sample) | Mech | Instruments
PR | Pressure (or Vacuum) Recorder | I&C | Instruments
PS | Pressure Switch / High, Low (Append with LL, L, H, or HH when needed) | I&C | Instruments
PIT | Pressure Transmitter (Delete “I” if not indicating) | I&C | Instruments
PTR | Printer | I&C | Instruments
QI | Quantity or Event Indicator (Electronic) | I&C | Instruments
QR | Quantity or Event Recorder | I&C | Instruments
SC | Sonic Horn | Mech | Instruments
SE | Speed Element | I&C | Instruments
SI | Speed Indicator (Electronic) | I&C | Instruments
SR | Speed Recorder | I&C | Instruments
SS | Speed Switch / High, Low (Append with H or L when needed) | I&C | Instruments
SIT | Speed Transmitter (Delete “I” if not indicating) | I&C | Instruments
TE | Temperature Element | I&C | Instruments
TG | Temperature Gauge | I&C | Instruments
TI | Temperature Indicator (Electronic) | I&C | Instruments
TR | Temperature Recorder | I&C | Instruments
TIT | Temperature Transmitter (Delete “I” if not indicating) | I&C | Instruments
TS | Temperature Switch / High, Low (Append with H or L when needed) | I&C | Instruments
TW | Thermowell | I&C | Instruments
VB | Vibration Cabinet | I&C | Instruments
VBR | Vibrator | Mech | Instruments
VD* | Vibration Driver (Replace * with axis or position, i.e., X, Y, Z, or K) | I&C | Instruments
VE* | Vibration Element (Replace * with axis or position, i.e., X, Y, Z, or K) | I&C | Instruments
VI* | Vibration Indication (Replace * with axis or position, i.e., X, Y, Z, or K) | I&C | Instruments
VR | Vibration Recorder | I&C | Instruments
VS** | Vibration Switch / High (Replace * with axis, i.e., X, Y, or Z, and/or H) | I&C | Instruments
VIT# | Vibration Transmitter (Delete “I” if not indicating) (Replace # with axis or position, i.e., X, Y, Z, or K) | I&C | Instruments
WE | Weight Element | I&C | Instruments
WI | Weight Indicator (electronic) | I&C | Instruments
WS | Weather Station | I&C | Instruments
WIT | Weight Transmitter (Delete “I” if not indicating) | I&C | Instruments
XDC | Transducer | I&C | Instruments
XS | Miscellaneous Switch (Shutdown) (Append with L or R when needed) | I&C | Instruments
YI | State or Event Indicator | I&C | Instruments
YS | State or Event Switch | I&C | Instruments
YT | State or Event Transmitter | I&C | Instruments
ZC | Position Controller | I&C | Instruments
ZE | Position Element | I&C | Instruments
ZI | Position Indicator (electronic) | I&C | Instruments
ZS | Position Signal - Limit Switch (Append with C=Closed, M=Middle, O=Open, L=Left, or R=Right; use A, B, C, . . . K or 1, 2, 3, . . . 10 for intermediate positions when needed) | I&C | Instruments
ZR | Position Recorder | I&C | Instruments
ZIT | Position Feedback Transmitter (Delete “I” if not indicating) | I&C | Instruments
BC | Bridge Crane | Mech | Miscellaneous Equipment
DO | Door | Various | Miscellaneous Equipment
EL | Elevator | Mech | Miscellaneous Equipment
EQ | Miscellaneous Equipment | Mech | Miscellaneous Equipment
EW | Eye Wash Station | Mech | Miscellaneous Equipment
GE | General Equipment | Mech | Miscellaneous Equipment
HE | Hoisting Accessories – miscellaneous (for example, slings and lifting beams) | Mech | Miscellaneous Equipment
HO | Hoist | Mech | Miscellaneous Equipment
JC | Jib Crane | Mech | Miscellaneous Equipment
LF | Lift Station | Mech | Miscellaneous Equipment
SA | Scale | Mech | Miscellaneous Equipment
SAF | Safety Shower | Mech | Miscellaneous Equipment
SX | Specialty Item | Mech | Miscellaneous Equipment
AP | Actuator (w/ motor) | Mech | Motors
HDD | Hydraulic Device Drive | Mech | Motors
HTM | Motor Heater | Elec | Motors
MC# * | Motor Control (Low Voltage) (Replace # with voltage letter) (Replace * with bus letter or number) | Elec | Motors
MO | Electrical Motor | Mech | Motors
VSD | Variable Speed Drive | Elec | Motors
CS | Chemical Seal (includes capillary-seal type isolators) | Mech | Piping
DK | Dry Pipe Sprinkler | Mech | Piping
DW | Ductwork | Mech | Piping
EX | Expansion Joint | Mech | Piping
FH | Flexible Hose | Mech | Piping
HDR | Header | Mech | Piping
IN | Insulation | Mech | Piping
IQ | Injection Quill | Mech | Piping
MN | Manifold | Mech | Piping
NZL | Nozzle | Mech | Piping
PAH | Pulse Air Header | Mech | Piping
PH | Pipe Hanger | Mech | Piping
PLGM | Mechanical Plug/Cap/Blank | Mech | Piping
PP | Piping | Mech | Piping
PPS | Pipe Sleeve | Mech | Piping
RO | Restriction Orifice | Mech | Piping
SEL | Seal | Mech | Piping
SF | Straightening Vane / Flow Straightener | Mech | Piping
SK | Stack | Mech | Piping
SL | Silencer | Mech | Piping
SPP | Spool Piece | Mech | Piping
SPR | Sprays – superheat, reheat, deck wash, pre-quench | Mech | Piping
WP | Wet Pipe Sprinkler | Mech | Piping
CRH | Crusher | Mech | Pulverizors
DL | Delumper | Mech | Pulverizors
GC | Clinker Grinder | Mech | Pulverizors
ML | Mill | Mech | Pulverizors
PL | Pulverizer | Mech | Pulverizors
PM | Pin Mill | Mech | Pulverizors
ED | Eductor | Mech | Pumps
EJ | Ejector | Mech | Pumps
HU | Heat Pump | Mech | Pumps
HV | Hydro Venturi Jet Pump | Mech | Pumps
JP | Jet Pump | Mech | Pumps
PU | Pump | Mech | Pumps
ACI | Aeration Unit – chemical injection | Mech | Skids
AHU | Air Handling Unit | Mech | Skids
CH | Chlorinator | Mech | Skids
CN | Conveyor | Mech | Skids
DC | Drag Chain | Mech | Skids
FD | Feeder | Mech | Skids
HPU | Hydraulic Power Unit | Mech | Skids
LU | Lubricator | Mech | Skids
PCS | Power Conversion System (SKID) | Elec | Skids
SD | Skid | Mech | Skids
SKR | Stacker | Mech | Skids
STP | Sewage Treatment Plant (whole assembly) | Mech | Skids
VAV | Variable Air Volume Terminal Unit | Mech | Skids
VC | Vacuum Cleaning Unit | Mech | Skids
AS | Absorber | Mech | Tanks_Vessels
AU | Accumulator | Mech | Tanks_Vessels
BA | Basin | Mech | Tanks_Vessels
BH | Baghouse | Mech | Tanks_Vessels
BK | Bunker | Mech | Tanks_Vessels
BN | Bin | Mech | Tanks_Vessels
CBX | Combiner Box | Elec | Tanks_Vessels
CES | Combination Safety Shower and Eye Wash Station | Mech | Tanks_Vessels
CF | Clarifier | Mech | Tanks_Vessels
CW | Catalyst | Mech | Tanks_Vessels
CY | Cyclone | Mech | Tanks_Vessels
DM | Demineralizer | Mech | Tanks_Vessels
DRM | Drum | Mech | Tanks_Vessels
GA | Gasifier | Mech | Tanks_Vessels
GTU | Geotube | Mechanical | Tanks_Vessels
HP | Hopper | Mech | Tanks_Vessels
MS | Magnetic Separator | Mech | Tanks_Vessels
OS | Oil Separator/Skimmer | Mech | Tanks_Vessels
OX | Oxidizer | Mech | Tanks_Vessels
PN | Polishing Unit | Mech | Tanks_Vessels
RCBX | Recombiner Box | Elec | Tanks_Vessels
RV | Air Receiver | Mech | Tanks_Vessels
RX | Reactor | Mech | Tanks_Vessels
SO | Silo | Mech | Tanks_Vessels
SP | Separator | Mech | Tanks_Vessels
STC | Storage Container Building | Mech | Tanks_Vessels
SU | Sump (typically concrete structure) | Mech | Tanks_Vessels
TC | Marshalling Cabinet | Elec | Tanks_Vessels
TK | Tank | Mech | Tanks_Vessels
VSL | Vessel (includes drain pots) | Mech | Tanks_Vessels
WDM | Water Deionization Module | Mech | Tanks_Vessels
TR#* | Transformer (Replace # with high side voltage letter) (Replace * with low side voltage letter) | Elec | Transformers
DN | Diesel Engine | Mech | Turbines
TU | Turbine | Mech | Turbines
AV | Analyzer Valve (w/ position interface) | Mech | Valves
CKV | Check Valve (Use when the complexity of the check valve is greater than the standard check valves that use equipment code VL) | Mech | Valves
CV | Control Valve (manual, no electrical control) | Mech | Valves
DV | Density Control Valve | Mech | Valves
EFV | Excess Flow Valve | Mech | Valves
EV | Electronic Relief Valve | Mech | Valves
FV | Flow Control Valve (w/ position interface) | Mech | Valves
HDC | Hydraulic Device Cylinder | Mech | Valves
HDW | Hand Wheel | Mech | Valves
HH | Hydrant | Mech | Valves
HL | Hydraulic Lift | Mech | Valves
LV | Level Control Valve (w/ position interface) | Mech | Valves
PNV | Pneumatic Actuated Valve | Mech | Valves
POS | Positioner | Mech | Valves
PV | Pressure Control Valve (including differential) (w/ position interface) | Mech | Valves
SRV | Safety Valve, Relief Valve, Safety-Relief Valve | Mech | Valves
SV | Solenoid Valve (Append with O for open, C for close, or append with nothing if the open/close indication is not required) | Mech | Valves
TP | Trap | Mech | Valves
TV | Temperature Control Valve (w/ position interface) | Mech | Valves
VL | Manual Hand Valve (includes simple check valves and other valve types with no electrical interface) | Mech | Valves
VN | Vent | Mech | Valves
VP | Manual Hand Valve with position indication (includes manual hand valves with limit switches) | Mech | Valves
XV | Isolation Valve with Operator | Mech | Valves
ZD | Position Device | Mech | Valves

## Instruments
Equipment Identification Number* | Equipment Description* | PSM asset?* | Manufacturer* | Model Number* | Serial Number* | Physical Location | Drawing Numbers* | Alternate ID 1* | Spare Parts List* | Project ID* | Type* | Voltage | Pressure Range [PSIG] | Temperature [F] Range | Loop No* | Level | Skid Reference/ID

## Breakers
Equipment Identification Number* | Equipment Description* | PSM asset?* | Manufacturer* | Model Number* | Serial Number* | Physical Location | Drawing Numbers* | Alternate ID 1* | Spare Parts List* | Project ID* | commodity type* | Voltage* | arc flash rating* | dual fed* | amp rating* | bus type* | protective relay type* | links | wires

## Cable
Equipment Identification Number* | Equipment Description* | PSM asset?* | Manufacturer* | Model Number* | Serial Number* | Physical Location | Drawing Numbers* | Alternate ID 1* | Spare Parts List* | Project ID* | commodity type* | Length | item | quantity3 | From asset* | To asset* | links | wires | from_terms | to_terms | Drawing Numbers

## Raceway
Equipment Identification Number* | Equipment Description* | PSM asset?* | Manufacturer* | Model Number* | Serial Number* | Physical Location* | Drawing Numbers* | Alternate ID 1* | Spare Parts List* | Project ID* | commodity type* | Length | links

## Batteries
Equipment Identification Number* | Equipment Description* | PSM asset?* | Manufacturer* | Model Number* | Serial Number* | Physical Location* | Drawing Numbers* | Alternate ID 1* | Spare Parts List* | Project ID* | commodity type* | Voltage* | arc flash rating* | dual fed* | amp rating* | bus type* | protective relay type* | PM number | links | wires | from_terms | to_terms

## Transformers
Equipment Identification Number* | Equipment Description* | PSM asset?* | Manufacturer* | Model Number* | Serial Number* | Physical Location* | Drawing Numbers* | Alternate ID 1* | Spare Parts List* | Project ID* | commodity type* | Liquid Temperature [F] range | Winding Temperature [F] range | dual fed* | Voltage in* | Voltage out* | amp rating* | protective relay type* | Capacity [] Rating* | Type* | Cooling Type* | Phase* | Mounting type* | PM number | pcb containing oil | oil Capacity [] | Vector group | Relays | links

## Pumps
Equipment Identification Number* | Equipment Description* | PSM asset?* | Manufacturer* | Model Number* | Serial Number* | Physical Location* | Drawing Numbers* | Alternate ID 1* | Spare Parts List* | Project ID* | Drive Type* | Material of Construction* | Size* | Flow Rate | RPM* | Design Pressure [PSIG] | Minimum Pressure [PSIG] | Operating Pressure [PSIG] | Maximum Pressure [PSIG] | Inlet Pressure [PSIG] | Outlet Pressure [PSIG] | Design Temperature [F] | Operating Temperature [F] | coupling type* | safety factor* | Mounting Position | Diameter | Capacity [] | Length | Skid Reference/ID

## Motors
Equipment Identification Number* | Equipment Description* | PSM asset?* | Manufacturer* | Model Number* | Serial Number* | Physical Location* | Drawing Numbers* | Alternate ID 1* | Spare Parts List* | Project ID* | Drive Type* | Material of Construction* | RPM* | Voltage* | Design Temperature [F] | Operating Temperature [F] | Rated Amps FLA* | Phase* | safety factor* | Horsepower* | Power Factor* | coupling type* | Mounting Position* | Insulation Spec | Insulation Type | Power | Heater Power | Locked Rotor Amps | Capacity [] | Service Factor | Enclosure Type | Length | Heater Voltage | Skid Reference/ID | Diameter

## Fans
Equipment Identification Number* | Equipment Description* | PSM asset?* | Manufacturer* | Model Number* | Serial Number* | Physical Location* | Drawing Numbers* | Alternate ID 1* | Spare Parts List* | Project ID* | Type* | Material of Construction | Drive Type* | Flow Rate* | RPM* | Supply Power Req'd* | Inlet Pressure [PSIG]* | Outlet Pressure [PSIG]* | Maximum Pressure [PSIG] | Design Pressure [PSIG] | Minimum Pressure [PSIG] | Operating Temperature [F] | Design Temperature [F] | Speed control* | bearing type* | Lube oil type | Skid Reference/ID | Enclosure Type

## Compressors
Equipment Identification Number* | Equipment Description* | PSM asset?* | Manufacturer* | Model Number* | Serial Number* | Physical Location* | Drawing Numbers* | Alternate ID 1* | Spare Parts List* | Project ID* | Type* | Material of Construction | Flow Rate* | RPM* | Supply Power Req'd* | Outlet Pressure [PSIG]* | Maximum Pressure [PSIG] | Design Pressure [PSIG] | Minimum Pressure [PSIG] | Inlet Pressure [PSIG] | Operating Temperature [F] | Design Temperature [F] | Cooling Type | bearing type | Lube oil type | Torque Power | Skid Reference/ID

## Generators
Equipment Identification Number* | Equipment Description* | PSM asset?* | Manufacturer* | Model Number* | Serial Number* | Physical Location* | Drawing Numbers* | Alternate ID 1* | Spare Parts List* | Project ID* | Type* | Material of Construction | Size* | Drive Type* | RPM* | Voltage* | Supply Power Req'd* | Maximum Pressure [PSIG] | Design Pressure [PSIG] | Minimum Pressure [PSIG] | Operating Temperature [F] | Design Temperature [F] | Excitation Voltage* | Power Factor* | Rated Amps FLA* | Phase* | Insulation Spec* | Insulation Type* | # Poles* | Cooling Type | bearing type | Lube oil type | Torque Power | Skid Reference/ID

## Turbines
Equipment Identification Number* | Equipment Description* | PSM asset?* | Manufacturer* | Model Number* | Serial Number* | Physical Location* | Drawing Numbers* | Alternate ID 1* | Spare Parts List* | Project ID* | Type* | Drive Type* | RPM* | Supply Power Req'd* | Exhaust Pressure [PSIG]* | Design Temperature [F] | Exhaust Temperature [F]* | Cooling Type | Torque Power | Sections | bearing type | Lube oil type

## HRSG
Equipment Identification Number* | Equipment Description* | PSM asset?* | Manufacturer* | Model Number* | Serial Number* | Physical Location* | Drawing Numbers* | Alternate ID 1* | Spare Parts List* | Project ID* | Type* | Size* | Design Temperature [F] | fuel type* | Sections | Cooling Type

## Boilers
Equipment Identification Number* | Equipment Description* | PSM asset?* | Manufacturer* | Model Number* | Serial Number* | Physical Location* | Drawing Numbers* | Alternate ID 1* | Spare Parts List* | Project ID* | Type* | Size* | Maximum Pressure [PSIG]* | Operating Temperature [F]* | Design Temperature [F] | MCR (Maximum continuous rating)* | fuel type* | Sections | Cooling Type

## Agitator_Mixers
Equipment Identification Number* | Equipment Description* | PSM asset?* | Manufacturer* | Model Number* | Serial Number* | Physical Location* | Drawing Numbers* | Alternate ID 1* | Spare Parts List* | Project ID* | Type* | Material of Construction | Size* | RPM* | Supply Power Req'd | Torque* | Horsepower* | Diameter* | Length* | Capacity [] | weight

## Gearboxes
Equipment Identification Number* | Equipment Description* | PSM asset?* | Manufacturer* | Model Number* | Serial Number* | Physical Location* | Drawing Numbers* | Alternate ID 1* | Spare Parts List* | Project ID* | Type* | Size* | Supply Power Req'd | Operating Temperature [F] | Output RPM* | Power* | input RPM* | Gear ratio* | bearing type* | mounting position* | Horsepower | Cooling Type

## Heat Exchangers_Vaporizers
Equipment Identification Number* | Equipment Description* | PSM asset?* | Manufacturer* | Model Number* | Serial Number* | Physical Location* | Drawing Numbers* | Alternate ID 1* | Spare Parts List* | Project ID* | Type* | Material of Construction | Flow Rate | Medium 1 Input/Output Pressure [PSIG]* | Medium 2 Input/Output Pressure [PSIG]* | Medium 2 Input/Output Temperature [F]* | Medium 1 Input/Output Temperature [F]* | Power*

## Tanks_Vessels
Equipment Identification Number* | Equipment Description* | PSM asset?* | Manufacturer* | Model Number* | Serial Number* | Physical Location* | Drawing Numbers* | Alternate ID 1* | Spare Parts List* | Project ID* | Type* | Material of Construction* | Maximum Pressure [PSIG] | Design Pressure [PSIG] | stored content* | Internal coating* | Diameter* | Length* | Capacity []* | Cathodic Protection Req'd?* | weight

## Dampers_Isolation Gates_Penstoc
Equipment Identification Number* | Equipment Description* | PSM asset?* | Manufacturer* | Model Number* | Serial Number* | Physical Location* | Drawing Numbers* | Alternate ID 1* | Spare Parts List* | Project ID* | Type* | Material of Construction* | Size* | Drive Type | Flow Rate | Maximum Pressure [PSIG] | Design Pressure [PSIG] | stored content* | Diameter* | Length* | depth* | weight

## Filters
Equipment Identification Number* | Equipment Description* | PSM asset?* | Manufacturer* | Model Number* | Serial Number* | Physical Location* | Drawing Numbers* | Alternate ID 1* | Spare Parts List* | Project ID* | Type* | Material of Construction* | Inlet Pressure [PSIG]* | Outlet Pressure [PSIG]* | Diameter* | Length* | width* | depth* | filtration rating* | Filter Class*

## Burners
Equipment Identification Number* | Equipment Description* | PSM asset?* | Manufacturer* | Model Number* | Serial Number* | Physical Location* | Drawing Numbers* | Alternate ID 1* | Spare Parts List* | Project ID* | Type* | Material of Construction | Size* | fuel type* | ignitor type* | weight

## Pulverizors
Equipment Identification Number* | Equipment Description* | PSM asset?* | Manufacturer* | Model Number* | Serial Number* | Physical Location* | Drawing Numbers* | Alternate ID 1* | Spare Parts List* | Project ID* | Type* | Material of Construction | Flow Rate | RPM* | Medium 1 Input/Output Temperature [F]* | Capacity []* | Horsepower* | bearing type* | weight

## Valves
Equipment Identification Number* | Equipment Description* | PSM asset?* | Manufacturer* | Model Number* | Serial Number* | Physical Location* | Drawing Numbers* | Alternate ID 1* | Spare Parts List* | Project ID* | Type* | Material of Construction* | Size* | Flow Rate | Design Pressure [PSIG] | Inlet Pressure [PSIG] | Outlet Pressure [PSIG] | Design Temperature [F] | Valve operator* | Fail Mode/position* | IO Type* | Control Range* | Motor Controller Voltage* | Skid Reference/ID* | Actuator Manufacturer* | Actuator Model Number* | Actuator Serial Number* | set point* | spring rating* | spring type*

## Piping
Equipment Identification Number* | Equipment Description* | PSM asset?* | Manufacturer* | Model Number* | Serial Number* | Physical Location* | Drawing Numbers* | Alternate ID 1* | Spare Parts List* | Project ID* | Material of Construction* | Size* | Fluid/Name* | Medium State* | Heat Trace* | Insulation Spec | Insulation Thk | Insulation Type | From asset | To asset | Coated | Coating System

## Skids
Equipment Identification Number* | Equipment Description* | PSM asset?* | Manufacturer* | Model Number* | Serial Number* | Physical Location* | Drawing Numbers* | Alternate ID 1* | Spare Parts List* | Project ID*

## Miscellaneous Equipment
Equipment Identification Number* | Equipment Description* | PSM asset?* | Manufacturer* | Model Number* | Serial Number* | Physical Location* | Drawing Numbers* | Alternate ID 1* | Spare Parts List* | Project ID*